## README
DRFC — Frequency & Primary-Frequency-Response (PFR) Parameters
Supplementary data for: Distributionally Robust Frequency-Constrained Dispatch of Microgrid Clusters with Shared Energy Storage
Item | Description
Purpose | Exact frequency-security and PFR parameters used in the case studies (Sections II-E, IV-D, V). Values are imported from the simulation code (config.py / frequency.py), not re-typed.
Systems | Two test systems: modified IEEE 33-bus / 4-MG and IEEE 123-bus / 6-MG.
Sheets | Freq_Security_Limits, SG_PFR, WT_PFR, ESS_PFR, MG_Aggregate.
Nominal frequency f0 | 50 Hz (50-Hz system).
Droop convention | Droop gain 1/R = Pmax / (R * f0) [MW/Hz]; a droop R=0.05 means a 5% frequency change deploys full reserve.
Inertia convention | Unit inertia contribution H * Pmax [MW*s] when committed; ESS virtual inertia H_e * P_max is shared equally across the cluster (/K).
Nominal point | Per-MG aggregates use a nominal islanding imbalance dP0 = 0.20 x peak load and the committed inertia H0 = 0.5*Sum(H*Pmax over SGs) + H_ess (floored at 1 MW*s), the linearisation point of the nadir constraint eq.(20).
Frequency metrics | RoCoF ¦dP¦/(2H) <= RoCoF_max; nadir f0-(dP/D)(1+sqrt(Tg/2H)) >= f_min; QSS ¦dP-dP_pfr¦/(D+Sum 1/R) <= df_qss,max.
Units | MW, MWh, MW/Hz, s, Hz, Hz/s as labelled in each header.
Note: derived per-MG quantities on the MG_Aggregate sheet are live Excel formulas referencing the unit sheets, so edits to any unit rating or droop propagate automatically.

## Freq_Security_Limits
Frequency-security limits & global constants (Section II-E-3)
Parameter | Symbol | Value | Unit | Paper ref.
Nominal frequency | f0 | 50 | Hz | Sec. II-E
RoCoF limit | RoCoF_max | 0.5 | Hz/s | eq. (13)
Frequency nadir floor | f_min | 49.5 | Hz | eq. (14)
Max allowable nadir drop | f0 - f_min | 0.5 | Hz | eq. (14)
Quasi-steady-state deviation cap | df_qss,max | 0.2 | Hz | eq. (16)
Load-damping coefficient (per peak-MW) | D_coef | 1 | MW/Hz per MW | eq. (10)
PFR discretisation time step | dt_PFR | 0.1 | s | eq. (19), Sec. V-A
PFR observation window | T_PFR | 30 | s | Sec. V-A
Per-MG load damping D = D_coef x (peak load of the MG); see MG_Aggregate.

## SG_PFR
Synchronous-generator governor & inertia parameters
System | MG | Unit | Pmax (MW) | Droop R | Tg (s) | H (s) | PFR reserve (MW) | 1/R (MW/Hz) | H*Pmax (MW*s) | Tg*Pmax
33-bus | 1 | SG1 | 3.5 | 0.05 | 8 | 4 | 1.75 | 1.4 | 14 | 28
33-bus | 2 | SG2a | 2.6 | 0.05 | 8 | 4 | 1.3 | 1.04 | 10.4 | 20.8
33-bus | 2 | SG2b | 2.4 | 0.05 | 8 | 4 | 1.2 | 0.96 | 9.6 | 19.2
33-bus | 3 | SG3 | 3 | 0.05 | 8 | 4 | 1.5 | 1.2 | 12 | 24
33-bus | 4 | SG4a | 2 | 0.05 | 8 | 4 | 1 | 0.8 | 8 | 16
33-bus | 4 | SG4b | 1.6 | 0.05 | 8 | 4 | 0.8 | 0.64 | 6.4 | 12.8
123-bus | 1 | SG1a | 3 | 0.05 | 8 | 4 | 1.5 | 1.2 | 12 | 24
123-bus | 1 | SG1b | 2 | 0.05 | 8 | 4 | 1 | 0.8 | 8 | 16
123-bus | 2 | SG2a | 3 | 0.05 | 8 | 4 | 1.5 | 1.2 | 12 | 24
123-bus | 2 | SG2b | 2 | 0.05 | 8 | 4 | 1 | 0.8 | 8 | 16
123-bus | 2 | SG2c | 1.5 | 0.05 | 8 | 4 | 0.75 | 0.6 | 6 | 12
123-bus | 3 | SG3a | 2.5 | 0.05 | 8 | 4 | 1.25 | 1 | 10 | 20
123-bus | 3 | SG3b | 1.5 | 0.05 | 8 | 4 | 0.75 | 0.6 | 6 | 12
123-bus | 4 | SG4a | 3 | 0.05 | 8 | 4 | 1.5 | 1.2 | 12 | 24
123-bus | 4 | SG4b | 2 | 0.05 | 8 | 4 | 1 | 0.8 | 8 | 16
123-bus | 5 | SG5a | 2.5 | 0.05 | 8 | 4 | 1.25 | 1 | 10 | 20
123-bus | 5 | SG5b | 2 | 0.05 | 8 | 4 | 1 | 0.8 | 8 | 16
123-bus | 5 | SG5c | 1.5 | 0.05 | 8 | 4 | 0.75 | 0.6 | 6 | 12
123-bus | 6 | SG6a | 2.5 | 0.05 | 8 | 4 | 1.25 | 1 | 10 | 20
123-bus | 6 | SG6b | 1.5 | 0.05 | 8 | 4 | 0.75 | 0.6 | 6 | 12

## WT_PFR
Wind-turbine deloading & PFR parameters
System | MG | Unit | Capacity (MW) | delta_max | Droop R | Tw (s) | H (s) | 1/R (MW/Hz)
33-bus | 1 | WT1 | 1.8 | 0.2 | 0.05 | 0.2 | 0 | 0.72
33-bus | 2 | WT2 | 2.7 | 0.2 | 0.05 | 0.2 | 0 | 1.08
33-bus | 3 | WT3 | 2 | 0.2 | 0.05 | 0.2 | 0 | 0.8
33-bus | 4 | WT4 | 1.6 | 0.2 | 0.05 | 0.2 | 0 | 0.64
123-bus | 1 | WT1 | 3 | 0.2 | 0.05 | 0.2 | 0 | 1.2
123-bus | 2 | WT2a | 2.5 | 0.2 | 0.05 | 0.2 | 0 | 1
123-bus | 2 | WT2b | 2 | 0.2 | 0.05 | 0.2 | 0 | 0.8
123-bus | 3 | WT3 | 2.5 | 0.2 | 0.05 | 0.2 | 0 | 1
123-bus | 4 | WT4 | 3 | 0.2 | 0.05 | 0.2 | 0 | 1.2
123-bus | 5 | WT5a | 2.5 | 0.2 | 0.05 | 0.2 | 0 | 1
123-bus | 5 | WT5b | 1.5 | 0.2 | 0.05 | 0.2 | 0 | 0.6
123-bus | 6 | WT6 | 2.5 | 0.2 | 0.05 | 0.2 | 0 | 1

## ESS_PFR
Shared energy storage (SESS): synthetic inertia & droop
System | E_max (MWh) | E_min (MWh) | P_max (MW) | eta_ch | eta_dis | H_e (s) | Droop R_e | Te_IR (s) | Te (s) | PFR reserve (MW) | K (MGs) | 1/R_e total (MW/Hz) | H_e*P_max (MW*s)
33-bus | 5 | 0.5 | 2 | 0.95 | 0.95 | 6 | 0.04 | 0.05 | 0.15 | 1.6 | 4 | 1 | 12
123-bus | 10 | 1 | 3 | 0.95 | 0.95 | 6 | 0.04 | 0.05 | 0.15 | 3.2 | 6 | 1.5 | 18
Per-MG ESS share: virtual inertia H_e*P_max/K and droop gain (1/R_e total)/K are allocated equally to each microgrid.

## MG_Aggregate
Per-microgrid aggregate frequency parameters (nominal operating point)
System | MG | Peak load (MW) | D (MW/Hz) | Tg_eq (s) | Sum H_SG (MW*s) | H_ess share (MW*s) | H0 (MW*s) | Sum 1/R (MW/Hz) | D+Sum 1/R (MW/Hz) | kappa0 (Hz/MW) | dP0 (MW) | g(dP0,H0) (Hz) | f_nadir (Hz)
33-bus | 1 | 2.4 | 2.4 | 8 | 14 | 3 | 10 | 2.37 | 4.77 | 0.34223 | 0.48 | 0.32649 | 49.6735
33-bus | 2 | 3 | 3 | 8 | 20 | 3 | 13 | 3.33 | 6.33 | 0.24561 | 0.6 | 0.31094 | 49.6891
33-bus | 3 | 1.8 | 1.8 | 8 | 12 | 3 | 9 | 2.25 | 4.05 | 0.41152 | 0.36 | 0.33333 | 49.6667
33-bus | 4 | 2.6 | 2.6 | 8 | 14.4 | 3 | 10.2 | 2.33 | 4.93 | 0.32986 | 0.52 | 0.32524 | 49.6748
123-bus | 1 | 5 | 5 | 8 | 20 | 3 | 13 | 3.45 | 8.45 | 0.18399 | 1 | 0.31094 | 49.6891
123-bus | 2 | 5.5 | 5.5 | 8 | 26 | 3 | 16 | 4.65 | 10.15 | 0.14778 | 1.1 | 0.3 | 49.7
123-bus | 3 | 4 | 4 | 8 | 16 | 3 | 11 | 2.85 | 6.85 | 0.23402 | 0.8 | 0.3206 | 49.6794
123-bus | 4 | 5 | 5 | 8 | 20 | 3 | 13 | 3.45 | 8.45 | 0.18399 | 1 | 0.31094 | 49.6891
123-bus | 5 | 4.5 | 4.5 | 8 | 24 | 3 | 15 | 4.25 | 8.75 | 0.1733 | 0.9 | 0.30328 | 49.6967
123-bus | 6 | 4 | 4 | 8 | 16 | 3 | 11 | 2.85 | 6.85 | 0.23402 | 0.8 | 0.3206 | 49.6794
g(dP0,H0) is the nadir drop at the nominal operating point; f_nadir = f0 - g. These are the Taylor-linearisation anchors of eq.(20).