## README
DRFC — Consolidated Initial Data
All inputs for: Distributionally Robust Frequency-Constrained Dispatch of Microgrid Clusters
Sheet | Contents
MG_Partition_33 | Microgrid bus partition, PCC, unit counts, peak load (33-bus)
Bus_Data_33 | Per-bus microgrid, active load, DER, role (33-bus)
Line_Data_33 | Branch R/X (ohm + p.u.), RCS tie-switches (33-bus)
DER_Placement_33 | Every DER: type, microgrid, bus, rating (33-bus)
SG_Parameters | Synchronous-generator parameters (both systems)
WT_Parameters | Wind-turbine parameters (both systems)
PV_Parameters | PV-array parameters (both systems)
Storage_SESS | Shared energy storage parameters (both systems)
Frequency_Limits | RoCoF / nadir / QSS limits and PFR settings
DRCC_Parameters | CVaR / Wasserstein / chance-constraint parameters
Cost_Coefficients | Generation, penalty, grid and UFLS cost coefficients
Sampling | Training/validation/test split, islanding events, seed
Benchmark_Methods | The eight compared methods and their settings
Penetration_Scenarios | Renewable-penetration sensitivity scenarios
Renewable_Data | Wind/solar data sources and generation method
Nominal_Profiles | 24-h nominal wind CF, PV CF, TOU price, load shapes
Renewable_ErrorStats | Per-hour forecast-error statistics (wind & PV)
System_123 | IEEE 123-bus / 6-MG partition and capacities
Base values: 12.66 kV, 10.0 MVA (Z_base=16.0276 ohm); nominal frequency f0=50 Hz; horizon 24 h (hourly).
Conventions: droop gain 1/R=Pmax/(R*f0) [MW/Hz]; unit inertia H*Pmax [MW*s]; shared-ESS inertia/droop split equally across K microgrids.

## MG_Partition_33
Microgrid partition (33-bus)
MG | Buses | #Buses | PCC | #SG | #WT | #PV | SG MW | WT MW | PV MW | Peak load MW
MG1 | 2, 3, 4, 5, 19, 20, 21, 22 | 8 | 2 | 1 | 1 | 1 | 3.5 | 1.8 | 1.2 | 2.4
MG2 | 14, 15, 16, 17, 18, 23, 24, 25 | 8 | 14 | 2 | 1 | 2 | 5 | 2.7 | 1.5 | 3
MG3 | 10, 11, 12, 13 | 4 | 18 | 1 | 1 | 1 | 3 | 2 | 1 | 1.8
MG4 | 6, 7, 8, 9, 26, 27, 28, 29, 30, 31, 32, 33 | 12 | 6 | 2 | 1 | 2 | 3.6 | 1.6 | 1.5 | 2.6
Bus 1 = substation / upstream grid (not in any MG). Peak load = aggregate per-MG demand used in the case study (data pipeline); the per-bus kW on Bus_Data_33 are the standard IEEE33 allocation weights.

## Bus_Data_33
Bus data (33-bus)
Bus | Microgrid | P load (kW) | DER(s) | Role
1 | Grid (substation) | 0 |  | substation/PCC
2 | MG1 | 100 |  | MG PCC
3 | MG1 | 90 | SG
4 | MG1 | 120 | PV
5 | MG1 | 60
6 | MG4 | 60 |  | MG PCC
7 | MG4 | 200 | SG
8 | MG4 | 200 | PV
9 | MG4 | 60
10 | MG3 | 60 | PV | MG PCC
11 | MG3 | 45 | SG
12 | MG3 | 60 | WT
13 | MG3 | 60
14 | MG2 | 120 | PV | MG PCC
15 | MG2 | 60
16 | MG2 | 60 | SG
17 | MG2 | 60 | WT
18 | MG2 | 90
19 | MG1 | 90
20 | MG1 | 90
21 | MG1 | 90 | WT
22 | MG1 | 90
23 | MG2 | 90 | PV
24 | MG2 | 420 | SG
25 | MG2 | 420
26 | MG4 | 60
27 | MG4 | 60
28 | MG4 | 60 | SG
29 | MG4 | 120
30 | MG4 | 200 | PV
31 | MG4 | 150 | WT
32 | MG4 | 210
33 | MG4 | 60

## Line_Data_33
Branch data (33-bus, standard IEEE 33-bus)
Z_base (ohm) = | 16.0276
From | To | R (ohm) | X (ohm) | R (pu) | X (pu) | Classification | RCS?
1 | 2 | 0.0922 | 0.047 | 0.0057526 | 0.0029324 | substation feeder
2 | 3 | 0.493 | 0.2511 | 0.03076 | 0.015667 | intra MG1
3 | 4 | 0.366 | 0.1864 | 0.022836 | 0.01163 | intra MG1
4 | 5 | 0.3811 | 0.1941 | 0.023778 | 0.01211 | intra MG1
5 | 6 | 0.819 | 0.707 | 0.051099 | 0.044112 | tie MG1-MG4 | yes
6 | 7 | 0.1872 | 0.6188 | 0.01168 | 0.038608 | intra MG4
7 | 8 | 0.7114 | 0.2351 | 0.044386 | 0.014668 | intra MG4
8 | 9 | 1.03 | 0.74 | 0.064264 | 0.04617 | intra MG4
9 | 10 | 1.044 | 0.74 | 0.065138 | 0.04617 | tie MG4-MG3 | yes
10 | 11 | 0.1966 | 0.065 | 0.012266 | 0.0040555 | intra MG3
11 | 12 | 0.3744 | 0.1238 | 0.02336 | 0.0077242 | intra MG3
12 | 13 | 1.468 | 1.155 | 0.091592 | 0.072063 | intra MG3
13 | 14 | 0.5416 | 0.7129 | 0.033792 | 0.04448 | tie MG3-MG2 | yes
14 | 15 | 0.591 | 0.526 | 0.036874 | 0.032818 | intra MG2
15 | 16 | 0.7463 | 0.545 | 0.046564 | 0.034004 | intra MG2
16 | 17 | 1.289 | 1.721 | 0.080424 | 0.10738 | intra MG2
17 | 18 | 0.732 | 0.574 | 0.045671 | 0.035813 | intra MG2
2 | 19 | 0.164 | 0.1565 | 0.010232 | 0.0097644 | intra MG1
19 | 20 | 1.5042 | 1.3554 | 0.093851 | 0.084567 | intra MG1
20 | 21 | 0.4095 | 0.4784 | 0.02555 | 0.029849 | intra MG1
21 | 22 | 0.7089 | 0.9373 | 0.04423 | 0.058481 | intra MG1
3 | 23 | 0.4512 | 0.3083 | 0.028152 | 0.019236 | tie MG1-MG2 | yes
23 | 24 | 0.898 | 0.7091 | 0.056028 | 0.044243 | intra MG2
24 | 25 | 0.896 | 0.7011 | 0.055904 | 0.043743 | intra MG2
6 | 26 | 0.203 | 0.1034 | 0.012666 | 0.0064514 | intra MG4
26 | 27 | 0.2842 | 0.1447 | 0.017732 | 0.0090282 | intra MG4
27 | 28 | 1.059 | 0.9337 | 0.066074 | 0.058256 | intra MG4
28 | 29 | 0.8042 | 0.7006 | 0.050176 | 0.043712 | intra MG4
29 | 30 | 0.5075 | 0.2585 | 0.031664 | 0.016128 | intra MG4
30 | 31 | 0.9744 | 0.963 | 0.060795 | 0.060084 | intra MG4
31 | 32 | 0.3105 | 0.3619 | 0.019373 | 0.02258 | intra MG4
32 | 33 | 0.341 | 0.5302 | 0.021276 | 0.033081 | intra MG4
1 | 18 | (added) | (added) |  |  | added tie Grid-MG2 | yes

## DER_Placement_33
DER placement & ratings (33-bus)
Unit | Type | MG | Bus | Rating (MW) | Key PFR params
SG1 | Synchronous generator | MG1 | 3 | 3.5 | R=0.05, Tg=8.0s, H=4.0s
WT1 | Wind turbine (deloaded) | MG1 | 21 | 1.8 | R=0.05, Tw=0.2s, dmax=0.2
PV1 | PV array | MG1 | 4 | 1.2 | -
SG2a | Synchronous generator | MG2 | 16 | 2.6 | R=0.05, Tg=8.0s, H=4.0s
SG2b | Synchronous generator | MG2 | 24 | 2.4 | R=0.05, Tg=8.0s, H=4.0s
WT2 | Wind turbine (deloaded) | MG2 | 17 | 2.7 | R=0.05, Tw=0.2s, dmax=0.2
PV2a | PV array | MG2 | 14 | 0.8 | -
PV2b | PV array | MG2 | 23 | 0.7 | -
SG3 | Synchronous generator | MG3 | 11 | 3 | R=0.05, Tg=8.0s, H=4.0s
WT3 | Wind turbine (deloaded) | MG3 | 12 | 2 | R=0.05, Tw=0.2s, dmax=0.2
PV3 | PV array | MG3 | 10 | 1 | -
SG4a | Synchronous generator | MG4 | 7 | 2 | R=0.05, Tg=8.0s, H=4.0s
SG4b | Synchronous generator | MG4 | 28 | 1.6 | R=0.05, Tg=8.0s, H=4.0s
WT4 | Wind turbine (deloaded) | MG4 | 31 | 1.6 | R=0.05, Tw=0.2s, dmax=0.2
PV4a | PV array | MG4 | 8 | 0.8 | -
PV4b | PV array | MG4 | 30 | 0.7 | -

## SG_Parameters
Synchronous-generator parameters
System | MG | Unit | Pmin MW | Pmax MW | Ramp+ MW/h | Ramp- MW/h | MinUp h | MinDn h | Cost $/MWh | NoLoad $/h | Droop R | Tg s | H s | Reserve MW
33-bus | MG1 | SG1 | 0.7 | 3.5 | 3.5 | 3.5 | 2 | 2 | 55 | 40 | 0.05 | 8 | 4 | 1.75
33-bus | MG2 | SG2a | 0.5 | 2.6 | 2.6 | 2.6 | 2 | 2 | 55 | 40 | 0.05 | 8 | 4 | 1.3
33-bus | MG2 | SG2b | 0.5 | 2.4 | 2.4 | 2.4 | 2 | 2 | 55 | 40 | 0.05 | 8 | 4 | 1.2
33-bus | MG3 | SG3 | 0.6 | 3 | 3 | 3 | 2 | 2 | 55 | 40 | 0.05 | 8 | 4 | 1.5
33-bus | MG4 | SG4a | 0.4 | 2 | 2 | 2 | 2 | 2 | 55 | 40 | 0.05 | 8 | 4 | 1
33-bus | MG4 | SG4b | 0.3 | 1.6 | 1.6 | 1.6 | 2 | 2 | 55 | 40 | 0.05 | 8 | 4 | 0.8
123-bus | MG1 | SG1a | 0.6 | 3 | 3 | 3 | 2 | 2 | 55 | 40 | 0.05 | 8 | 4 | 1.5
123-bus | MG1 | SG1b | 0.4 | 2 | 2 | 2 | 2 | 2 | 55 | 40 | 0.05 | 8 | 4 | 1
123-bus | MG2 | SG2a | 0.6 | 3 | 3 | 3 | 2 | 2 | 55 | 40 | 0.05 | 8 | 4 | 1.5
123-bus | MG2 | SG2b | 0.5 | 2 | 2 | 2 | 2 | 2 | 55 | 40 | 0.05 | 8 | 4 | 1
123-bus | MG2 | SG2c | 0.3 | 1.5 | 1.5 | 1.5 | 2 | 2 | 55 | 40 | 0.05 | 8 | 4 | 0.75
123-bus | MG3 | SG3a | 0.5 | 2.5 | 2.5 | 2.5 | 2 | 2 | 55 | 40 | 0.05 | 8 | 4 | 1.25
123-bus | MG3 | SG3b | 0.3 | 1.5 | 1.5 | 1.5 | 2 | 2 | 55 | 40 | 0.05 | 8 | 4 | 0.75
123-bus | MG4 | SG4a | 0.6 | 3 | 3 | 3 | 2 | 2 | 55 | 40 | 0.05 | 8 | 4 | 1.5
123-bus | MG4 | SG4b | 0.4 | 2 | 2 | 2 | 2 | 2 | 55 | 40 | 0.05 | 8 | 4 | 1
123-bus | MG5 | SG5a | 0.5 | 2.5 | 2.5 | 2.5 | 2 | 2 | 55 | 40 | 0.05 | 8 | 4 | 1.25
123-bus | MG5 | SG5b | 0.4 | 2 | 2 | 2 | 2 | 2 | 55 | 40 | 0.05 | 8 | 4 | 1
123-bus | MG5 | SG5c | 0.3 | 1.5 | 1.5 | 1.5 | 2 | 2 | 55 | 40 | 0.05 | 8 | 4 | 0.75
123-bus | MG6 | SG6a | 0.5 | 2.5 | 2.5 | 2.5 | 2 | 2 | 55 | 40 | 0.05 | 8 | 4 | 1.25
123-bus | MG6 | SG6b | 0.3 | 1.5 | 1.5 | 1.5 | 2 | 2 | 55 | 40 | 0.05 | 8 | 4 | 0.75

## WT_Parameters
Wind-turbine parameters
System | MG | Unit | Cap MW | delta_max | Droop R | Tw s | H s
33-bus | MG1 | WT1 | 1.8 | 0.2 | 0.05 | 0.2 | 0
33-bus | MG2 | WT2 | 2.7 | 0.2 | 0.05 | 0.2 | 0
33-bus | MG3 | WT3 | 2 | 0.2 | 0.05 | 0.2 | 0
33-bus | MG4 | WT4 | 1.6 | 0.2 | 0.05 | 0.2 | 0
123-bus | MG1 | WT1 | 3 | 0.2 | 0.05 | 0.2 | 0
123-bus | MG2 | WT2a | 2.5 | 0.2 | 0.05 | 0.2 | 0
123-bus | MG2 | WT2b | 2 | 0.2 | 0.05 | 0.2 | 0
123-bus | MG3 | WT3 | 2.5 | 0.2 | 0.05 | 0.2 | 0
123-bus | MG4 | WT4 | 3 | 0.2 | 0.05 | 0.2 | 0
123-bus | MG5 | WT5a | 2.5 | 0.2 | 0.05 | 0.2 | 0
123-bus | MG5 | WT5b | 1.5 | 0.2 | 0.05 | 0.2 | 0
123-bus | MG6 | WT6 | 2.5 | 0.2 | 0.05 | 0.2 | 0

## PV_Parameters
PV-array parameters
System | MG | Unit | Cap MW
33-bus | MG1 | PV1 | 1.2
33-bus | MG2 | PV2a | 0.8
33-bus | MG2 | PV2b | 0.7
33-bus | MG3 | PV3 | 1
33-bus | MG4 | PV4a | 0.8
33-bus | MG4 | PV4b | 0.7
123-bus | MG1 | PV1 | 2
123-bus | MG2 | PV2 | 2.5
123-bus | MG3 | PV3 | 1.5
123-bus | MG4 | PV4a | 2
123-bus | MG4 | PV4b | 1
123-bus | MG5 | PV5 | 2
123-bus | MG6 | PV6 | 1.5

## Storage_SESS
Shared energy storage (SESS)
System | E_max MWh | E_min MWh | P_max MW | eta_ch | eta_dis | SoC0 frac | Cyc $/MWh | H_e s | R_e | Te_IR s | Te s | Reserve MW | K
33-bus | 5 | 0.5 | 2 | 0.95 | 0.95 | 0.5 | 8 | 6 | 0.04 | 0.05 | 0.15 | 1.6 | 4
123-bus | 10 | 1 | 3 | 0.95 | 0.95 | 0.5 | 8 | 6 | 0.04 | 0.05 | 0.15 | 3.2 | 6

## Frequency_Limits
Frequency-security limits & PFR settings
Parameter | Symbol | Value | Unit
Nominal frequency | f0 | 50 | Hz
RoCoF limit | RoCoF_max | 0.5 | Hz/s
Nadir floor | f_min | 49.5 | Hz
QSS deviation cap | df_qss,max | 0.2 | Hz
Load-damping coefficient | D_coef | 1 | MW/Hz per peak-MW
PFR time step | dt_PFR | 0.1 | s
PFR window | T_PFR | 30 | s

## DRCC_Parameters
DRCC / Wasserstein / CVaR parameters
Parameter | Symbol | Value | Note
CVaR risk level (initial) | alpha^(0) | 0.1 | start of alternating minimization
CVaR risk level (operating) | alpha | 0.12 | after alternating minimization
Wasserstein radius (operating) | epsilon | 0.1 | N=300 (see Sampling)
Confidence level | beta | 0.05 | finite-sample guarantee
Frequency chance budget | eta | 0.05 | joint freq violation budget
System chance budget | gamma | 0.05 | power-balance / line budget
Effective dimension | d_eff | 2 | in radius formula eq.(15)
Support diameter | diam(Xi) | 1 | radius formula constant
Radius constants | c1, c2 | 1.0, 1.0 | radius formula constants

## Cost_Coefficients
Cost coefficients
Parameter | Symbol | Value | Unit
Load-shedding penalty | C_shed | 2000 | $/MWh
Renewable-curtailment penalty | C_curt | 50 | $/MWh
Reserve-violation penalty | C_res | 500 | $/MW
Grid import price | C_buy | 120 | $/MWh
Grid export price | C_sell | 60 | $/MWh
WT O&M / curtailment opportunity | c_WT | 5 | $/MWh
PV O&M | c_PV | 0 | $/MWh
Max sheddable load fraction | kappa_max | 0.3 | -
Value of lost load (UFLS) | C_ufls | 12000 | $/MWh
Islanding probability weight | p_island | 0.7 | -
UFLS load block per event | - | 0.18 | fraction of load

## Sampling
Scenario sampling & evaluation
Item | Value | Note
Training samples N | 300 | empirical Wasserstein distribution
Validation samples | 65 | out-of-sample radius/alpha tuning
Test scenarios | 100 | out-of-sample cost evaluation
Islanding events | 100 | random islanding events for frequency check
Total historical days | ~365 | common aligned PV+wind days (Tronder record)
Random seed | 2024 | reproducibility
Sample-size sweep | 50,100,200,300,400,500 | Table III sensitivity

## Benchmark_Methods
Compared methods (eight)
Method | Description / setting
DET | Deterministic dispatch on forecasts; no uncertainty handling.
SO | Scenario stochastic optimization; 100 Monte-Carlo scenarios from an assumed normal distribution.
RO | Budget-based robust optimization; conservatism parameter Gamma = 5.
CVaR-SO | CVaR-constrained SO on the empirical distribution (no Wasserstein ball).
Box-RO | Interval robust optimization; each uncertain parameter in its observed min-max range, no budget.
DRCC-no-FC | Proposed DRCC with the frequency constraints removed (ablation).
No-Sharing | Each MG has dedicated storage of equal total capacity (1.25 MWh / 0.5 MW per MG); no sharing (ablation).
Prop. (DRCC) | Proposed Wasserstein DRCC with joint frequency chance constraints and shared storage.

## Penetration_Scenarios
Renewable-penetration sensitivity
Scenario | Renewable penetration | Note
Low | 30% | renewable forecast energy / total daily load
Base | 50% | nominal case (Tables I-IV, VI)
High | 70% | stress case for high renewable uncertainty

## Renewable_Data
Wind / solar data: sources & generation method
Dataset | Resolution | Coverage | Role
Tronder Energi AI hackathon 2021 (train.csv) | Hourly | 396 days | Primary source: actual PV/wind/consumption + NWP weather features; basis of the day-ahead forecast and forecast-error samples; spot-market price shape.
50-prosumer PV & load | 15-min | 50 prosumers + 40 EVs | Reference load magnitudes / spatial load diversity across microgrids.
NREL wind speed (5-min, 2008-2012) | 5-min | 2008-2012 | Auxiliary wind-speed reference.
PV + external temperature 2019 | 5-min | Full year 2019 | Auxiliary PV-generation reference.
Market clearing prices | Hourly | 2025 | Auxiliary price reference.
Forecast & forecast-error generation method:
1. Normalise actual PV/wind to capacity factors (CF in [0,1]) using the 99.5th percentile as capacity.
2. Fit a ridge regression (lambda=5, standardised features) of CF on NWP features to obtain the day-ahead forecast P_hat:
PV features: clear_sky_rad, global_rad, direct_rad, diffuse_rad, sun_elevation, effective_cloud_cover.
Wind features: wind_speed_100m/50m/10m, temperature, relative_humidity_100m.
3. Forecast-error samples xi = (actual CF - forecast CF) per day x hour; scaled by unit capacity (MW) and err_scale = 1.4.
4. Nominal day-ahead forecast = median daily forecast profile (see Nominal_Profiles).
5. Spatial heterogeneity: per-MG time-of-day roll (mg_phase_span = 12 h) and history-day roll (spatial_day_offset = 60 d)
decorrelate cross-MG shortfalls -> complementary uncertainty -> shared-storage value.
6. Split the resulting day samples into N_train = 300 / N_valid = 65 (and 100 test scenarios); seed = 2024.

## Nominal_Profiles
24-h nominal profiles (capacity factors / normalised)
Hour | Wind CF | PV CF | TOU price (norm, mean=1) | Load: industrial (norm) | Load: general (norm)
0 | 0.37 | 0 | 0.6387 | 0.3478 | 0.3617
1 | 0.3649 | 0 | 0.6387 | 0.3478 | 0.3617
2 | 0.3499 | 0 | 0.639 | 0.3478 | 0.3617
3 | 0.3261 | 0 | 0.6408 | 0.348 | 0.3617
4 | 0.295 | 0 | 0.6496 | 0.3491 | 0.3618
5 | 0.2588 | 0 | 0.682 | 0.3565 | 0.3623
6 | 0.22 | 0 | 0.772 | 0.3888 | 0.3653
7 | 0.1812 | 0.2381 | 0.9576 | 0.4853 | 0.3762
8 | 0.145 | 0.46 | 1.2307 | 0.6743 | 0.4045
9 | 0.1139 | 0.6505 | 1.4866 | 0.8964 | 0.4551
10 | 0.0901 | 0.7967 | 1.563 | 1 | 0.5131
11 | 0.0751 | 0.8887 | 1.3772 | 0.8965 | 0.5489
12 | 0.07 | 0.92 | 1.0205 | 0.6753 | 0.5521
13 | 0.0751 | 0.8887 | 0.6893 | 0.4916 | 0.5539
14 | 0.0901 | 0.7967 | 0.5368 | 0.4184 | 0.5996
15 | 0.1139 | 0.6505 | 0.6043 | 0.4582 | 0.7041
16 | 0.145 | 0.46 | 0.856 | 0.606 | 0.84
17 | 0.1812 | 0.2381 | 1.2119 | 0.8242 | 0.9551
18 | 0.22 | 0 | 1.5382 | 0.9962 | 1
19 | 0.2588 | 0 | 1.6772 | 0.9962 | 0.9544
20 | 0.295 | 0 | 1.5595 | 0.824 | 0.8365
21 | 0.3261 | 0 | 1.2723 | 0.6047 | 0.6897
22 | 0.3499 | 0 | 0.9779 | 0.4496 | 0.5571
23 | 0.3649 | 0 | 0.7801 | 0.3774 | 0.4621
Wind/PV CF are the designed nominal day-ahead shapes (x installed capacity = forecast MW); data-derived forecast errors (Renewable_Data) are added on top. Price x C_buy = $/MWh.

## Renewable_ErrorStats
Forecast-error statistics (capacity-factor residuals)
Hour | Wind CF error std | PV CF error std
0 | 0.1565 | 0
1 | 0.1648 | 0.0023
2 | 0.1568 | 0.0039
3 | 0.1495 | 0.013
4 | 0.1504 | 0.0329
5 | 0.1469 | 0.0458
6 | 0.1506 | 0.0499
7 | 0.1455 | 0.0894
8 | 0.1467 | 0.1314
9 | 0.1437 | 0.1655
10 | 0.1406 | 0.1889
11 | 0.1471 | 0.2087
12 | 0.1645 | 0.1761
13 | 0.1691 | 0.1524
14 | 0.1717 | 0.1184
15 | 0.1663 | 0.0888
16 | 0.1652 | 0.0731
17 | 0.1663 | 0.0719
18 | 0.1553 | 0.0545
19 | 0.1542 | 0.0291
20 | 0.1557 | 0.0122
21 | 0.1498 | 0.0033
22 | 0.1352 | 0
23 | 0.1446 | 0
Overall forecast RMSE (CF): wind=0.1548, PV=0.1018; days=396. Errors scaled by err_scale=1.4 and unit capacity to MW.

## System_123
IEEE 123-bus / 6-MG system
MG | Buses | #SG | SG MW | #WT | WT MW | #PV | PV MW | Peak MW
MG1 | 1-20 | 2 | 5 | 1 | 3 | 1 | 2 | 5
MG2 | 21-42 | 3 | 6.5 | 2 | 4.5 | 1 | 2.5 | 5.5
MG3 | 43-64 | 2 | 4 | 1 | 2.5 | 1 | 1.5 | 4
MG4 | 65-85 | 2 | 5 | 1 | 3 | 2 | 3 | 5
MG5 | 86-105 | 3 | 6 | 2 | 4 | 1 | 2 | 4.5
MG6 | 106-123 | 2 | 4 | 1 | 2.5 | 1 | 1.5 | 4
Totals: installed generation 62.5 MW; peak load 28 MW; shared storage 10 MWh / 3 MW.